## Case details
Energy Memo: GLA Consultation
Case details
Date of first review: | 2020-06-04
Case Name: | 20-24 Pope's Road
Case Number: | 2021/0265 (2020/6774) (5276)
Case Officer: | Toyin Omodara
London Borough: | Lambeth
Application Type (Outline/Hybrid/Detailed): | Detailed
Applicant: | AG Hondo Popes Road BV
Energy Consultant: | Hurley Palmer Flatt
Document Title: | Energy Statement
Document Date: | 2020-03-01
Development proposals
Use | Floorspace/Number of units
B1 & A1/3 | 28139 m2

## Pre-application advice
1 | Draft London Plan: The Mayor has published his Intend to Publish version of the new London Plan which includes new carbon, energy and heat risk policies (See Policies SI 2, SI 3 and SI 4). Please ensure that you are aware of these new policies in preparation for submitting your planning application. The latest status of the draftnew London Plan can be found here: https://www.london.gov.uk/what-we-do/planning/london-plan/new-london-plan/what-new-london-plan.
2 | Guidance: Applicants should follow the GLA Energy Assessment Guidance 2018 (https://www.london.gov.uk/sites/default/files/energy_assessment_guidance_2018_-_update.pdf) which sets out the information that should be provided within the energy assessment to be submitted at Stage 1. Please note that an updated 2020 version of this guidance has been published on the GLA’s website in draft form which aligns with the new London Plan carbon, energy and heat risk policies (https://www.london.gov.uk/sites/default/files/gla_energy_assessment_guidance_april_2020.pdf). Applicants should ensure they are familiar with the new guidance in preparation for submitting their planning application.
3 | The following comments summarise key points for you to be aware of in progressing your energy strategy, but you should refer to the guidance for full details.
Net zero carbon target
4 | The Mayor’s draft London Plan requires all major developments (residential and non-residential) to meet his net-zero carbon target. This should be met with a minimum on-site 35% reduction in carbon emissions beyond Part L of 2013 Building Regulations with any carbon shortfall to net zero being paid into the relevant borough’s carbon offset fund.
5 | Applicants should submit a completed Carbon Emissions Reporting spreadsheet (https://www.london.gov.uk/what-we-do/planning/planning-applications-and-decisions/pre-planning-application-meeting-service-0) alongside their Stage 1 application to confirm the anticipated carbon performance of the development and should clearly set out the carbon emission factors they are proposing to use in their energy assessment. Although results for both sets of carbon emission factors should be submitted, applicants are encouraged to use the SAP 10.0 carbon emission factors for referable applications when estimating CO2 emission performance against London Plan policies. However, for developments in Heat Network Priority Areas with the potential to connect to a planned or existing district heating network (DHN) the SAP 2012 emission factors may be used provided that the heat network operator has developed, or is in the process of developing, a strategy to decarbonise the network which has been agreed with the GLA.
6 | The carbon emission figures should be reported against a Part L 2013 baseline. Sample SAP full calculation worksheets (both DER and TER sheets) and BRUKL sheets for all stages of the energy hierarchy should be provided to support the savings claimed.
Be Lean Demand Reduction
7 | Applicants are expected to meet the London Plan energy efficiency targets:
• Residential – at least a 10% improvement on 2013 Building Regulations from energy efficiency
• Non-residential – at least a 15% improvement on 2013 Building Regulations from energy efficiency
8 | Applicants will be expected to consider and minimise the estimated energy costs to occupants and outline how they are committed to protecting the consumer from high prices. See the guidance for further detail.
Cooling and Overheating
9 | The Good Homes Alliance (GHA) Early Stage Overheating Risk Tool (https://goodhomes.org.uk/wp-content/uploads/2019/07/GHA-Overheating-in-New-Homes-Tool-and-Guidance-Tool-only.pdf) should be submitted to the GLA alongside the Stage 1 application, if this was not submitted at pre-application stage, to identify potential overheating risk and passive responses early in the design process.
10 | Evidence should be provided on how the demand for cooling and the overheating risk will be minimised through passive design in line with the cooling hierarchy. Dynamic overheating modelling in line with CIBSE Guidance should be carried out (TM59 for residential and TM52 for non-residential) for all TM49 weather scenarios.
11 | The area weighted average (MJ/m2) and total (MJ/year) cooling demand for the actual and notional building should be provided and the applicant should demonstrate that the actual building’s cooling demand is lower than the notional.
Be Clean Heating Infrastructure
12 | The applicant should investigate opportunities for connection to nearby existing or planned district heating networks (DHNs). Where such opportunities exist, this should be the priority for supplying heat to the site in line with the London Plan heating hierarchy. Evidence of this investigation should be provided including evidence of active two-way communication with the network operator, the local authority and other relevant parties. This should include information on connection timescales and confirmation that the network has available capacity. See the guidance for full details on the information that should be provided.
13 | The site should be provided with a single point of connection and a communal heating network where all buildings/uses on site will be connected. Relevant drawings/schematics demonstrating the above should be provided.
14 | The applicant should provide evidence confirming that the development is future proofed for connection to wider district networks now or in the future, where an immediate connection is not available.
15 | Where a DHN connection is not available, either now or in the future, applicants should follow the London Plan heating hierarchy to identify a suitable communal heating system for the site.
16 | The draft London Plan limits the role of CHP to low-emission CHP and only in instances where it can support the delivery of an area-wide heat network at large, strategic sites. Applicants proposing to use low-emission CHP will be asked to provide sufficient information to justify its use and strategic role while ensuring that the carbon and air quality impact is minimised.
Be Green Renewable Energy
17 | All major development proposals should maximise opportunities for renewable energy generation by producing, using and storing renewable energy on-site. This is regardless of whether the 35% on-site target has already been met through earlier stages of the energy hierarchy.
18 | Solar PV should be maximised. Applicants should submit the total PV system output (kWp) and a plan showing that the proposed installation has been maximised for the available roof area and clearly outlining any constraints to further PV.
19 | Should heat pumps be proposed, applicants will be expected to demonstrate a high specification of energy efficiency measures under be lean, a thorough performance analysis of the heat pump system and, where there are opportunities for DHN connection, that the system is compatible. The detail submitted on heat pumps should include: a. An estimate of the heating and/or cooling energy (MWh/annum) the heat pumps would provide to the development and the percentage of contribution to the site’s heat loads. b. Details of how the Seasonal Coefficient of Performance (SCOP) and Seasonal Energy Efficiency ratio (SEER) has been calculated for the energy modelling. This should be based on a dynamic calculation of the system boundaries over the course of a year i.e. incorporating variations in source temperatures and the design sink temperatures (for space heat and hot water). c. The expected heat source temperature and the heat distribution system temperature with an explanation of how the difference will be minimised to ensure the system runs efficiently. The distribution loss factor should be calculated based on the above information and used for calculation purposes. d. Whether any additional technology is required for top up or during peak loads (e.g. hot water supply) and how this has been incorporated into the energy modelling assumptions.
Carbon Offsetting
20 | Applicants should maximise carbon emission reductions on-site. Where it is clearly demonstrated that no further carbon savings can be achieved, but the site falls short of the carbon reduction targets, applicants are required to make a cash-in-lieu contribution to the relevant boroughs’ carbon offset fund using the GLA’s recommended carbon offset price or, where a local price has been set, the borough’s’ carbon offset price.
21 | Energy strategies should provide a calculation of the shortfall in carbon emissions and the offset payment that will be made to the borough.
New London Plan policies (for information)
22 | Applicants will be expected to investigate the potential for energy flexibility in new developments, include proposals to reduce the amount of capacity required for each site and to reduce peak demand. The measures followed to achieve this should be set out in their energy assessment. See the 2020 guidance for further details.
23 | Applicants will be expected to calculate and reduce whole life-cycle carbon emissions to fully capture the development’s carbon footprint. Applicants should submit a whole life-cycle carbon assessment to the GLA as part of the Stage 1 application submission, following the Whole Life-Cycle Carbon Assessment Guidance and using the GLA’s reporting template (https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/planning-guidance/whole-life-cycle-carbon-assessments-guidance-pre-consultation-draft). Applicants will also be conditioned to submit a post-construction assessment to report on the development’s actual WLC emissions.
24 | Applicants will be expected to monitor on their development’s energy performance and report on it through an online monitoring portal. Applicants should review the ‘Be seen’ energy monitoring guidance to ensure that they are fully aware of the relevant requirements to comply with the ‘be seen’ policy (https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/planning-guidance/be-seen-energy-monitoring-guidance-pre-consultation-draft). A commitment should be provided that the development will be designed to enable post construction monitoring and that the information set out in the ‘be seen’ guidance is submitted to the GLA’s portal at the appropriate reporting stages. This will be secured through suitable legal wording.

## Energy Comments
Comment No. | GLA Stage I | Applicant's Stage I response | GLA Post Stage I response | Applicant's Post Stage I response | GLA Post Stage I response | Applicant's Post Stage I response | GLA Post Stage I response (Stage 3) | Applicant's Post Stage I response | GLA Post Stage I response (Stage 3) | Applicant's Post Stage I response | GLA Post Stage I response (Stage 3) | Applicant Response
| Date: 04/06/2020 | Date: 17/11/20 | Date: 23/11/20 | Date: 27/11/20 | Date: 07/12/20 |  | Date: 16/12/21 |  | Date: 21/12/21 | Date 22/12/2022 | Date: 23/12/21
General compliance comments
[7 empty] | The applicant's response to GLA's energy comments should be provided directly within this Energy Memo. Any wider supporting material submitted but be referenced within the applicant's memo repsonse. |  | The applicant's response to GLA's energy comments should be provided directly within this Energy Memo. Any wider supporting material submitted but be referenced within the applicant's memo repsonse.
3 | The applicant should submit the GLA’s Carbon Emission Reporting spreadsheet, which has been developed to allow the use of the updated SAP 10 emission factors alongside the SAP 2012 emission factors. The link to the spreadsheet can be found here: https://www.london.gov.uk/what-we-do/planning/planning-applications-and-decisions/pre-planning-application-meeting-service-0] | No response | The applicant should submit the GLA’s Carbon Emission Reporting spreadsheet, which has been developed to allow the use of the updated SAP 10 emission factors alongside the SAP 2012 emission factors. The link to the spreadsheet can be found here: https://www.london.gov.uk/what-we-do/planning/planning-applications-and-decisions/pre-planning-application-meeting-service-0] This item is outstanding. | Spreadsheet based on original Energy Statement attached. | The speadsheet is welcomed. However, the validation columns (E and F) should be matching for all stages of the energy hierarchy. Notably, the Be Lean stage is significantly different. This should be reviewed and an updated spreadsheet submitted with all validation columns matching. This should be updated to address item 17/18. This item is outstanding. |  | No response located within the submission files. This item is outstanding. |  | The updated spreadsheet should be submitted. This item is outstanding. | Pelase refer to the WED14106 - Pope's Road gla_carbon_emission_reporting_spreadsheet submitted | The spreadsheet could not be located the applicant should resubmit this. This item is outstanding. | The spreadhsheet was sent on 05.01.2022
Be Lean
Overheating
Be Clean
9 | The applicant has carried out an investigation and there are no existing or planned district heating networks within the vicinity of the proposed development. They should contact relevant stakeholders including the borough energy officer, local heat network operators and nearby developers and ask whether they know of any local heat network connection opportunities. | No response | The applicant should contact relevant stakeholders including the borough energy officer, local heat network operators and nearby developers and ask whether they know of any local heat network connection opportunities. Evidence of the correspondence should be submitted. This item is outstanding. | The energy statement makes reference to local heat networks in section 4.6.1 ‘Connection to an area wide network’. A desktop feasibility study was conducted using the GLA London Heat Map to explore connection opportunities within relative proximity to the proposed development. It was identified that the district heating network in Lambeth is approximately 1.3km away when based on an appropriate trenching route as such, this has been deemed unfeasible. The map illustration attached shows the route proceeding northbound from the site onto Brixton Road (A23) then diverting onto Loughborough Road before a connection on Evandale Road. | The desktop study is welcomed, however, the applicant is also required to contact relevant stakeholders - as a minimum the borough energy officer - and ask whether they know of any local heat network connection opportunities. Evidence of the correspondence should be submitted. This item is outstanding. |  | No response located within the submission files. This item is outstanding. |  | The applicant has provided evidence of correspondence with the network operator, that confirmed there are no plans for expansion. This is welcomed. They should also contact the borough energy officer and ask whether they know of any local heat network connection opportunities. This item is outstanding. | We have contacted the Energy Officer from the Lambeth council Tony Cook and awaiting feedback on the query . | This is welcomed. The applicant should submit the response of the borough energy officer when available. This item is outstanding. | HDR is still awaiting a response from the energy officer
10 | The applicant has provided a commitment that the development is designed to allow future connection to a district heating network. Drawings demonstrating how the site is to be future-proofed for a connection to a district heating network should be provided. This should include a single point of connection to the district heating network. | No response | Drawings demonstrating how the site is to be future-proofed for a connection to a district heating network should be provided. This should include a single point of connection to the district heating network. This item is outstanding. | A single point of connection can be accomodated in the common basement of the development within the Basement AHU plantroom (basement block plantroom layout attached). This area has direct access to the site boudary for connection to any future district hetwork running along the north service road. This position also avoids using the busier south boundary where HV run alongside the access road. | Nothing further required.
11 | The applicant should propose a communal heat system supplied by a centralised plant room. It should be confirmed that all non-domestic building uses (includuing the retail) will be connected to the communal heat system. A drawing showing the route of the heat network linking all uses on the site should be provided alongside a drawing indicating the floor area, internal layout and location of the energy centre. |  | The applicant should propose a communal heat system supplied by a centralised plant room. It should be confirmed that all non-domestic building uses (includuing the retail) will be connected to the communal heat system. A drawing showing the route of the heat network linking all uses on the site should be provided alongside a drawing indicating the floor area, internal layout and location of the energy centre. This item is outstanding. | The main heating system proposed is composed of air source heat pumps connected to LTHW networks serving the two office blocks. The west block heat pumps also serve the dedicated high temperature ASHP for the domestic hot water. It is anticipated that the two office systems are kept separate to reduce distribution lenght and losses, since efficiency gains of a combined system were expected to be minor. The differences in load profiles and horus of operation of the small retail units at the market space under the building was deemed incompatible with the central heat pump system; as such each unit has been provided with space for installation of its own DX unit for heating and (if requried) cooling. A heating/cooling diagramatic schematic as well as plant room block layouts is attached. | In this instance, the separate heating / cooling systems to suit different profiles is accepted. Nothing further required.
Be Green
14 | The applicant is not proposing to install any renewable energy technology for the development. The GLA expects all major development proposals to maximise on-site renewable energy generation, where feasible. This is regardless of whether the 35% on-site CO2 emission improvement target has already been reached through earlier stages of the energy hierarchy. The applicant is, therefore, required to reinvestigate the inclusion of renewable technologies. A roof layout should be provided to demostrate that there is no potential for PV as concluded within the energy statement. | As part of the amendment to the planning application submitted to Lambeth, we have identified an area on the east block roof for incorporation of Photovoltaic panels (plan attached). The west block roof is occupied by MEP heat rejection equipment and façade access equipment, unsuitable for PVs. | The incorporation of PV is welcomed. However, the cited roof layout has not been received. A detailed roof layout covering all roofs should be provided demonstrating that the roof’s potential for a PV installation has been maximised. They should confirm the kWp of Photovoltaic (PV) panels m2 of net PV area and kWh of electricity generation. The on-site savings from renewable energy technologies should be maximised regardless of the London Plan targets having been met. This item is outstanding. | The original plantroom block layouts for all roofs are included and show that the west block roof is occupied by a double-stacked MEP equipment and unsuitable for PVs. A preliminary roof area of 240m2 on teh East Block has therefore been identified for the installation of solar PV panels as indicated in the atatched roof plan. Below are calcualtions fro potential energy generation of this space. The following calculations are based on indicative figures and have not considered solar mapping studies to comprehensively explore feasibility of the PV array. Proposed PV panel area = 1.68m2 per panel We would typically recommend half of the proposed area is allocated for solar panels. This allows for appropriate spacing/orientation of the PV array, allowance for maintenance/cleaning walkways and minimising the potential risk of overshading from adjacent plant. Therefore, 240m2/2 = 120m2 120m2/1.68m2 = 71 panels approximately. The performance of each panel has been based on a ‘Sunmodule Bisun protect 290W’ PV unit – specification sheet attached for information. 290W x 71 PV panels = 20.59kWp. PV generated electricity = 18,554kWh per year | It is unclear whether further area may be available for PV and this should be clarified in further detail with indicative PV panel layout and a set of roof drawings clearly showing the constraints to PV to all other areas. Higher efficiency panels should be proposed and kWp, kWh and kWh of renewable energy generation should be confirmed. The applicant should be conditioned to demonstrate that PV has been maximised prior to the commencement of works on site and again prior to occupation. This item is outstanding. |  | No response located within the submission files. This item is outstanding. |  | It is unclear whether further area may be available for PV and this should be clarified in further detail with indicative PV panel layout and a set of roof drawings clearly showing the constraints to PV to all other areas. Higher efficiency panels should be proposed and kWp, kWh and kWh of renewable energy generation should be confirmed. The applicant should be conditioned to demonstrate that PV has been maximised prior to the commencement of works on site and again prior to occupation. This item is outstanding. | Please refer to the section 4.7.2 of the HDR submitted energy strategy (DEc 2021) which states the following :” The final proposals include a 21.44 kWp Photovoltaic (PV) arrays that are predicting an annual yield of 17,728 kWh translating to a carbon saving 4,130 kgCO2/annum” . Please find attached the roof layout which shows that the roof space has been maximised to accommodate the PV system and that highly efficient panels of 320Watt peak each have been used. | The roof layout and the proposal of high efficient 320 Watt PV panels are welcomed, however there appears to be further additional space for PV on the east block roof. The applicant should confirm also that as suggested before the west block roof will be used for mechanical plant and whether they have considered the inclusion of PVs on any green/brown roof areas using biosolar arrangement and how PV can be integrated with any amenity areas. A condition for this to be demonstrated prior to commencement and occupation would be accepted. This item is outstanding. | The roof of the East block is cover by the plantroom which is open to the outside and therefore PV panels cannot be included in this area. The PV area has been maximised to avoid overshadowing from plant area. Therefore no further pv can be fitted.
15 | Heat pumps are being proposed in the form of a (centralised) Air to water heat pumps. Further information on the heat pumps should be provided including: a. An estimate of the heating and/or cooling energy (MWh/annum) the heat pumps would provide to the development and the percentage of contribution to the site’s heat loads. b. Details of how the Seasonal Coefficient of Performance (SCOP) and Seasonal Energy Efficiency ratio (SEER) has been calculated for the energy modelling. This should be based on a dynamic calculation of the system boundaries over the course of a year i.e. incorporating variations in source temperatures and the design sink temperatures (for space heat and hot water). c. The expected heat source temperature and the heat distribution system temperature with an explanation of how the difference will be minimised to ensure the system runs efficiently. The distribution loss factor should be calculated based on the above information and used for calculation purposes. d. Whether any additional technology is required for top up or during peak loads (e.g. hot water supply) and how this has been incorporated into the energy modelling assumptions. | a. Based on the BRUKL output, the estimated heating and cooling demand for the building is 96.61MJ/m2 and they have confirmed the estimated heating and cooling energy consumption by the heat pumps. The heat pumps will cover 100% of the site heat loads (there is no other heat source proposed). b. SCoP and SEER values used in the energy model were based on manufacturers technical specification for indicative units (see attached example of one of the specification sheets provided by Mitsubishi). c. The primary LTHW circuit is expected to operate at 55C/45C. As design develops, consideration will be given to the use of intermediate high-temperature water-to-water heat pump secondary circuits to serve air-handling units, enabling operating temperature range of fan-coil units secondary circuits to be reduced to 45C/40C, if technically feasible. d. No additional technology is required. Hydraulically independent secondary circuits will be provided to deliver LTHW to the office fan-coil unit system, central air handling units and the domestic hot water high-temperature heat pumps. A high-temperature water-to-water heat pump will be used to lift LTHW from 55C to 75C for distribution to indirect heating coils within the domestic hot water storage cylinders. | a. Nothing further required. b. The datasheet has not been received. This should be submitted. This item is outstanding. c. Nothing further required. d. Nothing further required. | Datasheet attached | The datasheet submitted appears to only address cooling. A datasheet that also addresses heating is required. This item is outstanding. |  | No response located within the submission files. This item is outstanding. |  | The datasheet submitted appears to only address cooling. A datasheet that also addresses heating is required. This item is outstanding. |  | The applicant has submitted the datasheet that includes heating and contains a COP of 2.5 for heating. The applicant should make sure that this COP was used in modelling. Nothing further is required here.
Please refer to the document i-FX-Q2-G05_-XL-CA_-0802.pdf attached
Carbon performance and offsetting
17 | The carbon dioxide savings fall short of the on-site target within the London Plan. The applicant should consider the scope for additional measures aimed at achieving further carbon reductions/In this instance it is accepted that there is little further potential for carbon dioxide reductions onsite. | As part of the amendment to the planning application submitted to Lambeth, we have committed to reach a minimum on-site 35% regulated carbon emissions reductions during the design development at later RIBA stages. Additional measures considered to achieve this further reduction are: - Photovoltaics on the east block roof - Improved plant efficiencies. Furthermore, the applicant is committed to signing up to renewable electricity to reduce the building carbon emissions. | This is welcomed. However, further detail on the proposed improved plant efficiencies and updated CO2 emissions are required to support the improved performance. PV will be addressed in item 14. This item is outstanding. | The details of improved plant efficiency and additional on-site generation from PVs are not available at the moment as these proposed enhancements have not been modelled. The Energy Statement submitted with the planning application and the attached GLA Carbon Emission Rerporting Spreadhseet includes the details of the modelled design. The additional enhancements are a commitment the applicant made to the local authority and will be detailed and modelled at the next design stage to demonstrate the achieved carbon emissions. | Updated modelling should be undertaken at the current stage in order to estimate the impact of the proposed measures. This item cannot be closed until this has been addressed. The carbon offset payment should be agreed with the borough and evidence of the correspondene provided confirming the agreed approach. This item is outstanding. |  | No response located within the submission files. This item is outstanding. |  | Updated Addendum Energy Statement has updated modelling with additional energy measures and now achieves the minimum on-site target emissions within the London Plan of 35%. This is welcomed. The applicant should submit the GLA carbon emissions reporting spreadsheet and clearly present the additional measures that were added on top of the previous strategy. This item is outstanding. | Pelase refer to the WED14106 - Pope's Road gla_carbon_emission_reporting_spreadsheet submitted | The spreadsheet could not be located the applicant should resubmit this. This item is outstanding. | The spreadsheet was sent on 05.01.2022
18 | The applicant should confirm the carbon shortfall in tonnes CO2 and the associated carbon offset payment that will be made to the borough. | The shortfall and associated carbon offset according to the massing in January and the GLA worksheet used to calculate it is £22,005 (table below). Since then, an amendment was submitted where the applicant committed to reaching the London Plan target of 35% regulated carbon dioxide savings on-site. In this case no offset payment would be due.
New London Plan policies (for information) | [8 empty] | This item is outstanding.
19 | (Upon the LP publication), the applicant should submit/has submitted a WLC assessment which will be reviewed separately; comments will be provided. The WLC assessment should follow the GLA WLC guidance (https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/planning-guidance/whole-life-cycle-carbon-assessments-guidance-pre-consultation-draft).
20 | The applicant will be expected to review the ‘Be seen’ energy monitoring guidance (https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/planning-guidance/be-seen-energy-monitoring-guidance-pre-consultation-draft) early in the design process to ensure that they are fully aware of the relevant requirements to comply with the ‘be seen’ policy. A commitment should be provided that the development will be designed to enable post construction monitoring and that the information set out in the ‘be seen’ guidance is submitted to the GLA’s portal at the appropriate reporting stages. This will be secured through suitable legal wording.
Other points
Move resolved comments under this section
1 | The energy strategy is generally compliant with the London Plan policies however, the applicant is required to submit the additional information, which has been requested below. |  | This item will be addressed through response to all other items. Nothing further requried here.
2 | For the purposes of this assessment, the applicant will be estimating the CO2 emission performance against London Plan policies using the SAP 10 emissions factors. This is supported. |  | Nothing further required.
5 | Based on the information provided, the non-domestic element of the proposed development is estimated to achieve a reduction of 66.7 tonnes per annum (19%) in regulated CO2 emissions compared to a 2013 Building Regulations compliant development. |  | Nothing further required.
8 | The area weighted average (MJ/m2) and total (MJ/year) cooling demand for the actual and notional building has been provided and the applicant has demonstrated that the actual building’s cooling demand is lower than the notional. |  | Nothing further required.

## CO2 performance
Domestic
SAP 2012 / SAP 10 (please specify) | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations
Energy Efficiency |  | 0 | #DIV/0!
CHP |  | 0 | #DIV/0!
Renewable energy |  | 0 | #DIV/0!
Total |  | 0 | #DIV/0!
Non-domestic
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations | 346.8
Energy Efficiency | 272.1 | 74.7 | 21.54%
CHP | 272.1 | 0 | 0%
Renewable energy | 210.5 | 61.6 | 17.76%
Total |  | 136.3 | 39.3%
Carbon offsetting
| Shortfall (tonnes per annum) | Shortfall (£)
Domestic
Non-domestic |  | 0
Total | 0 | 0