# Energy Assessment Guidance – Appendix 5 Overheating Checklist

# Building 3

| Section 1 - Site features affecting vulnerability to overheating |  | Response |
| --- | --- | --- |
| Site location | Urban – within central London or in a high density conurbation Peri-urban – on the suburban fringes of London | Urban – central London (RBKC) |
| Air quality and/or Noise sensitivity – are any of the following in the vicinity of buildings? | Busy roads / A roads | A roads |
|  | Railways / Overground / DLR | Railways/overground |
|  | Airport / Flight path | N/A |
|  | Industrial uses / waste facility | N/A |
| Proposed building use | Will any buildings be occupied by vulnerable people (e.g. elderly, disabled, young children)? | Yes |
|  | Are residents likely to be at home during the day (e.g. students)? | No |
| Dwelling aspect | Are there any single aspect units? | Yes |
| Glazing ratio | Is the glazing ratio (glazing: internal floor area) greater than 25%? | No, 19.45% |
|  | If yes, is this to allow acceptable levels of daylighting? | - |
| Security - Are there any security issues that could limit opening of windows for ventilation? | Single storey ground floor units | Yes |
|  | Vulnerable areas identified by the Police Architectural Liaison Officer | No |
|  | Other | N/A |

| Section 2 - Design features implemented to mitigate overheating risk |  | Response |
| --- | --- | --- |
| Landscaping | Will deciduous trees be provided for summer shading (to windows and pedestrian routes)? | Yes |
|  | Will green roofs be provided? | Yes – planted amenity roof |
|  | Will other green or blue infrastructure be provided around buildings for evaporative cooling? | Yes – extensive soft landscaping at podium level |
| Materials | Have high albedo (light colour) materials been specified? | Yes |
| Dwelling aspect | % of total units that are single aspect | 44% |
|  | % single aspect with N / NE / NW orientation | 12% |
|  | % single aspect with E orientation | 0% |
|  | % single aspect with S / SE / SW orientation | 32% |
|  | % single aspect with W orientation | % |
| Glazing ratio - What is the glazing ratio (glazing; internal floor area) on each facade? | N / NE / NW | 10.26% |
|  | E | 0% |
|  | S / SE / SW | 9.19% |
|  | W | 0% |
| Daylighting | What is the average daylight factor range? | 0.8% to 4.5% on the lowest 11 floors. Detailed ‘per room’ results can be found within Annex 5 of the ES Chapter |
| Window opening | Are windows openable? | Yes |
| Window opening | What is the average percentage of openable area for the windows? | 43.75% |
| Window opening - What is the extent of the opening? | Fully openable | Balcony doors only |
|  | Limited (e.g. for security, safety, wind loading reasons) | Apart from balcony sliding doors, windows are limited to 100mm for safety reasons |
| Security | Where there are security issues (e.g. ground floor flats) has an alternative night time natural ventilation method been provided (e.g. ventilation grates)? | Yes |
| Shading | Is there any external shading? | Yes – Some protruding and inset balconies provide shading to unit below |
|  | Is there any internal shading? | Yes – light coloured blinds |
| Glazing specification | Is there any solar control glazing? | Yes - G value: 0.5 |

| Ventilation - What is the ventilation strategy? | Natural – background | Yes – openable windows |
| --- | --- | --- |
|  | Natural – purge | Yes - perforated brick ventilation panel with a 50% openable area and insulated door is provided in addition to façade openings to rooms requiring additional means of natural ventilation. |
|  | Mechanical – background (e.g. MVHR) | Yes |
|  | Mechanical – purge | Yes |
|  | What is the average design air change rate | Trickle ventilation as per part F table 5.1b; purge at 4 ACH |
| Heating system | Is communal heating present? | Yes |
|  | What is the flow/return temperature? | 70-40˚C |
|  | Have horizontal pipe runs been minimised? | Yes |
|  | Do the specifications include insulation levels in line with the London Heat Network Manual | Yes |